## Instructions
City of Concord
Technical Requirements Workbook
Instructions
Proposer shall respond to each requirement on each tab (Green) based on the response options provided in the"Proposer Response" column via pull down menu. If additional explanation is required, proposer shall fill out Column F, "Proposer Comment".
A detailed description of each priority set by the utility is provided in the 'Priority' tab. The right is reserved to modify prioritization of requirements at any point and without notice to Proposers.
A detailed description of each response option is provided in the 'Response Options' tab.

## Priority
City of Concord
Technical Requirements
Priority
Priority | Description
Critical | This function is of the highest priority to addressing current operational needs at the utility; however, solutions that do not have high priority items in the current base solution will not be disqualified.
Optional | This function would be nice to have but does not present an immediate concern to the overall operational or implementation needs of the utility.

## Response Options
City of Concord
Technical Requirements
Response Options
Vendor Response | Description
Current Base | The function is provided in the base product today. No modification is required. The pricing proposed encompasses this function.
Future Base Release | The function will be provided in a future base release that will be a general release within 18 months from submission of this response. No modification or customization is required, and no additional fees are needed for implementation. Vendor will indicate timing of when desired functionality will be available and make a statement of whether or not the vendor is agreeable to representing this function as a requirement in the final contract.
Partially Comply | This function can be supported in some manner by: providing alternative functionality; implementing an additional module; or by modifying an existing screen, existing view, or existing report. The function would not cause a change in the system source code and would not break the system upgrade path. The pricing proposed encompasses this function. A comment must be given explaining how the solution partially complies.
Not Provided | This function is not provided by the vendor in the proposed solution. The pricing proposed does not encompass this function.
Not Applicable | This function is not relevant due to the specifics of what is being proposed due to underlying technology differences (e.g., a requirement that would only apply to a cellular-based solution whereas the solution proposed is not cellular-based). Those requirements listing this response will be highly scrutinized for appropriateness, and the right is reserved to add or subtract points based on this response, at the discretion of the awarding body.

## AMI FAN
ID | Category | Commodity | Priority | Requirement | RF Based | Proposer Response | Proposer Comment | Column1
1 | Administration | All | Critical | Provide administrator tools and console for the administration and monitoring of the application.
2 | Administration | All | Critical | Provide export of all interval and register usage data, alarms, and events.
3 | Administration | All | Critical | Provide tools or applications for users to create and export custom reports.
4 | Administration | All | Critical | Have the ability to archive and purge data according to a data strategy.
5 | Administration | All | Critical | Collect all interval data and logs from meters and Communications Network components at a configurable frequency, but at least once per day.
6 | Administration | All | Critical | Support centralized remote management, monitoring, graphical monitoring, and control of all network hardware. | O
7 | Administration | All | Critical | Support centralized remote management, monitoring, graphical monitoring, and control of all endpoint hardware.
8 | Administration | All | Critical | Be capable of remotely detecting network communications problems including loss of redundant communications pathways, diminishing signal strength, or poor interval performance. | O
9 | Administration | All | Critical | Be capable of remotely correcting system/component problems, which at a minimum shall include the ability to remotely recycle (or restart) a component. | O
10 | Administration | Electric | Critical | Support an power status verification for electric meters by meter/customer or batch of meters/customers, via the user interface.
11 | Administration | All | Critical | Support automatic discovery of all new endpoint devices.
12 | Administration | All | Critical | Support automatic and/or programmatic discovery of communications equipment (repeaters, collectors / concentrators, etc.). | O
13 | Administration | All | Critical | Have capability to automatically perform a last read of interval and register data, before a configuration update is performed
14 | General | All | Critical | Provide separate production and test environments for the AMI headend System prior to go-live.
15 | General | All | Critical | Provision separate production and test environments for the AMI headend System for the duration of the contract.
16 | General | All | Critical | Provide context-sensitive system documentation for online user help.
17 | General | All | Critical | Have a non-proprietary database file structure that is ODBC-compliant and SQL-compliant, and provided by a standard commercial database supplier
18 | General | All | Critical | Provide a minimum of 12 months of online storage for all AMI endpoint data collected.
19 | Functionality | All | Critical | Be capable of performing on-demand read requests to retrieve events, usage and register data.
20 | Functionality | All | Critical | Be able to distinguish between a missing interval and zero consumption and provide reporting capability for missing data or gaps.
21 | Functionality | All | Critical | Track devices with missing data due to failed or incomplete communications and provide an automatic retry process to ensure several efforts are made to capture missing interval data for endpoints.
22 | Functionality | All | Critical | Log all messages sent to and received from all AMI components with the message date/time, event/message type identifier, and source/target(s) identifier.
23 | Functionality | All | Critical | Log each instance when an event message has been sent to an AMI component, but no acknowledgement is received within the configured time frame.
24 | Functionality | All | Critical | Process Standard Time and Daylight Savings Time changes across system devices.
25 | Functionality | All | Critical | Process leap year changes across system devices.
26 | Functionality | All | Optional | Have the capability to assign internal user-specific screen presentation criteria (i.e. personalized home dashboard) based on user sign-in (role-based presentation).
27 | Functionality | All | Critical | Support user capability to export report and query data in CSV, SQL, Excel, XML, TXT, or other flat-file formats.
28 | Functionality | All | Critical | Support a variety of number of dials that contain up to 9 digits on register read.
29 | Functionality | All | Critical | Support 9-digit length serial number for meter or endpoint.
30 | Electric Meter - Demand | Electric | Critical | Send acknowledgement to AMI headend of demand reset function has been preformed, along with time stamp of reset.
31 | Electric Meter - Demand | Electric | Critical | Be configurable to record 5-minute, 15-minute, 30-minute and 60-minute demand values based on a rolling basis.
32 | Electric Meter - Demand | Electric | Optional | Automatically reset the meter peak demand register on the billing cycle date, configurable to the utility's billing calendar.
33 | Electric Meter - Demand | Electric | Optional | Remotely reset the meter peak demand register on the scheduled day for off-cycle events, such as move-in or move-out.
34 | Electric Meter - Demand | Electric | Optional | Be able to accept and process a remote demand reset command from the AMI headend system >99% of the time.
35 | Electric Meter - Demand | Electric | Critical | Deliver the daily peak demand value, and, after midnight each day, reset the demand register.
36 | Electric Meter - Demand | Electric | Critical | Provide a time stamp with the peak demand recorded for the period set in the metrology of the meter, for demand-enabled meters.
37 | Electric Meter - Demand | Electric | Critical | Support reporting power factor at time of each: peak kW; peak kVA and; peak kVAR.
38 | Electric Meter - Functionality | Electric | Critical | Support configurable display registers with at least 6 (digits) plus 2 decimals.
39 | Electric Meter - Functionality | Electric | Critical | Support bi-directional (net) electric flow metering for measurement and collection of delivered and received real and reactive energy consumption, demand, interval data, and time of use.
40 | Electric Meter - Functionality | Electric | Critical | Have sensors to detect hot socket/overvoltage and temperature.
41 | Electric Meter - Functionality | Electric | Critical | Perform a diagnostic self-test upon start up and in the event of errors or warnings report the error on the meter display and provide notification back to the AMI headend.
42 | Electric Meter - Functionality | Electric | Critical | Log a date/time stamped event when an operation occurs, with a message to communicate success or failure, for meters with service disconnect switches.
43 | Electric Meter - Functionality | Electric | Critical | Be capable of operating at its maximum rated load without overflowing the interval data counter, no matter the interval length selected.
44 | Electric Meter - Functionality | Electric | Critical | Be able to support remote configuration of the kWh read interval.
45 | Electric Meter - Functionality | Electric | Critical | Be able to measure 5-minute, 15-minute, 30-minute and 60-minute block demand (KW).
46 | Electric Meter - Functionality | Electric | Critical | Be able to deliver the daily peak demand (KW) and reset the demand at midnight each day.
47 | Electric Meter - Functionality | Electric | Critical | Be able to measure and deliver power factor.
48 | Electric Meter - Functionality | Electric | Critical | Be able to support remote configuration of the kW read interval.
49 | Electric Meter - Functionality | Electric | Critical | Be available to be retrofit with a KYZ pulse output board without limiting AMI functionality, for three-phase meters.
50 | Electric Meter - Functionality | Electric | Critical | For residential meters, be able to provide load profile register/interval data for the following units of measure in configurable 15, 30 & 60 minute intervals with time stamp: kWh delivered, kWh received, kW delivered, and kW received.
51 | Electric Meter - Functionality | Electric | Critical | For bellwhether metering to support conversation voltage reduction, support 1-minute voltage profiling transmitted in 5-minute intervals.
52 | Electric Meter - Functionality | Electric | Critical | For commercial meters, be able to provide load profile register/interval data for the following units of measure in configurable 5, 15, 30 & 60 minute intervals with time stamp: kWh delivered, kWh received, kW delivered, kW recieved, kVARh delivered, kVARh received, kVA delivered, and voltage.
53 | Electric Meter - Functionality | Electric | Critical | Provide voltage per phase.
54 | Electric Meter - Functionality | Electric | Critical | Provide amperage per phase.
55 | Electric Meter - Functionality | Electric | Critical | Store interval data and daily read data including date and time stamps for a minimum of 45 days in module memory for 15-minute interval data.
56 | Electric Meter - Functionality | Electric | Critical | Be capable of identifying service type/form factor.
57 | Electric Meter - Functionality | Electric | Critical | Provide a phase angle measurement both positive (leading angle) and negative (lagging angle), for three-phase meters.
58 | Electric Meter - Functionality | Electric | Critical | Provide an instantaneous amperage reading on demand, and maximum amperage for interval readings.
59 | Electric Meter - Functionality | Electric | Critical | Provide an instantaneous voltage reading on demand, and max/min voltage reading for interval readings.
60 | Electric Meter - Functionality | Electric | Critical | Provide an event denoting the date/time field access was performed or attempted.
61 | Electric Meter - General | Electric | Critical | Be supplied with a scannable manufacturer serial number bar code label, including the electric meter number affixed to the meter faceplate.
62 | Electric Meter - General | Electric | Critical | Provide electronic vendor meter inventory file with meter deliveries.
63 | Electric Meter - General | Electric | Critical | Provide a field tool and related software for diagnostic purposes and to provide the capabilites to download register and interval data from the meters/endpoints as well as update the meter programs and firmware.
64 | Electric Meter - General | Electric | Critical | Provide security/authentication for local AMI meter data exchange to ensure that data exchanges can only be executed by authorized users or users authorized with designated field tools.
65 | Electric Meter - General | Electric | Critical | Keep time even if there is no communication with the AMI system.
66 | Electric Meter - HAN | Electric | Optional | Be available with an optional Zigbee radio for Personal Area Network (PAN) or Home Area Network (HAN), for residential meters.
67 | Electric Meter - HAN | Electric | Optional | Be available with an optional alternative protocol (non-Zigbee) radio for Personal Area Network (PAN) or Home Area Network (HAN), for residential meters.
68 | Electric Meter - Load Limiting | Electric | Optional | Have the ability to support current/load limiting functionality, for residential disconnect meters.
69 | Electric Meter - Load Limiting | Electric | Optional | Be able to accept and process a remote load limiting command from the AMI Head-end system, for load limiting-supported meters.
70 | Electric Meter - Load Limiting | Electric | Optional | Be able to send an acknowledgement of the current state of load limiting status, for load limiting-supported meters.
71 | Remote Disconnect | Electric | Critical | Be available with an optional service disconnect switch capable of interrupting up to 200 amps, for residential meters (Form 2S class 320 meters excepted).
72 | Remote Disconnect | Electric | Optional | Be available with an optional service disconnect switch capable of interrupting up to 300 amps.
73 | Remote Disconnect | Electric | Optional | Be available with a button or lever to enable the service disconnect switch to close when the 'Arm to Connect" option is used for reconnecting service remotely, for residential meters.
74 | Electric Meter - TOU | Electric | Critical | Provide the capability to create and maintain Time of Use schedules (at least 10) for the purpose of enabling and updating TOU schedules in electric meters.
75 | Electric Meter - TOU | Electric | Critical | Support at least 4 separate daily time bands for TOU schedules (e.g., on peak, off peak, mid peak, and shoulder peaks).
76 | Electric Meter - TOU | Electric | Critical | Implement seasonal TOU schedule changes on a specified date.
77 | Electric Meter - TOU | Electric | Critical | Be capable of implementing over the air updates of TOU schedules to electric meters belonging to specific program groups.
78 | Electric Meter - TOU | Electric | Critical | Be capable of retreiving and storing TOU registers.
79 | Electric Meter - TOU | Electric | Critical | Be capable of exporting TOU register readings along with interval data and other register readings.
80 | Endpoints | Water | Critical | Be capable of configuring endpoints to deliver either hourly or 15-minute interval reads.
81 | Endpoints | Water | Critical | Have the ability to time stamp and align intervals in accordance with: a) for hourly intervals, on the hour; b) for 15 minute intervals, on the 15, 30, 45 and 60 minute clock positions.
82 | Endpoints | Water | Optional | Have the ability to have alternate method of capturing reads when unable to do so using the fixed network.
83 | Endpoints | All | Critical | Provide a means for extracting stored data directly from the device in the event of network communications or equipment failure.
84 | Endpoints | Water | Critical | Be designed to have a failure rate of less than 0.5 % per year.
85 | Endpoints | Water | Critical | Store interval data and daily read data including date and time stamps for a minimum of 45 days in module memory for hourly interval data.
86 | Endpoints | Water | Critical | Be designed and constructed to have a life expectancy of at least 20 years.
87 | Endpoints | Water | Critical | Be rated for performance of at least IP68 conditions or better.
88 | Endpoints | Water | Critical | Be supplied with a scannable bar code label affixed to the endpoint.
89 | Endpoints | Water | Critical | Support local data exchange of all AMI communications data and logs.
90 | Endpoints | Water | Critical | Provide security/authentication for local AMI meter data exchange to ensure that data exchanges can only be executed by authorized users or users authorized with designated field tools.
91 | Endpoints | Water | Critical | Keep time even if there is no communication with the AMI system.
92 | Event/Alarm Management | All | Critical | Identify or flag events/alarms that require further investigation or field resolution.
93 | Event/Alarm Management | All | Critical | Be configurable to analyze received events and alarms and initiate creation of service orders or other exceptions.
94 | Event/Alarm Management | All | Critical | Provide mechanism to automatically communicate a certain event and/or alarm to designated recipients via email.
95 | Event/Alarm Management | All | Optional | Provide mechanism to automatically communicate a certain event and/or alarm to designated recipients via SMS.
96 | Event/Alarm Management | All | Critical | Have the ability to forward selected events or alarms, once received, to another application as necessary to support distribution operations and monitoring.
97 | Event/Alarm Management | All | Critical | Store all events and alarms for display to the user and for analysis using queries and reports.
98 | Event/Alarm Management | All | Critical | Allow for configuration or custom events or alarms based on analytics or calculation (e.g. continuous consumption), rather than a report.
99 | Event/Alarm Management | All | Critical | Detect, timestamp, and report removal of an endpoint (cut wire).
100 | Event/Alarm Management | Electric | Critical | Detect, timestamp, and report meter tilt/tamper, for meters with the capability to detect tilt.
101 | Event/Alarm Management | All | Critical | Detect, timestamp, and report stopped/dead/non-registering meters.
102 | Event/Alarm Management | All | Critical | Detect, timestamp, and report rollover events.
103 | Event/Alarm Management | All | Critical | Detect, timestamp, and report reverse flow on meters not operating as net or bi-directional meters.
104 | Event/Alarm Management | All | Critical | Support user-defined global threshholds (i.e., thresholds for all meters) for alarms/events based on nominal values.
105 | Event/Alarm Management | All | Critical | Support user-defined local threshholds (i.e., thresholds by individual meter or batch of meters) for alarms/events based on nominal values.
106 | Event/Alarm Management | All | Critical | Support user-defined prioritization of events to allow critical traffic to have priority.
107 | Event/Alarm Management | All | Critical | Support ability to configure whether an event/alarm is transmitted instantaneously or with a regularly scheduled batch of readings and event data.
108 | Event/Alarm Management | All | Critical | Be able to report high priority messages within thirty seconds 90% of the time.
109 | Event/Alarm Management | All | Critical | Be able to report medium priority messages 90% of the time.
110 | Event/Alarm Management | All | Critical | Be able to report low priority messages 90% of the time.
111 | Event/Alarm Management | All | Critical | Automatically resend event notification until a message is acknowledged by the AMI headend.
112 | Event/Alarm Management | All | Critical | Detect and log access by any field device (e.g., optical port, Bluetooth connection, etc.).
113 | Event/Alarm Management | Electric | Critical | Detect, timestamp, and report the loss of power, defined as the reduction of line-side voltage of at least some percentage of nominal voltage for a programmable number of continuous seconds (nominally 60 seconds).
114 | Event/Alarm Management | Electric | Critical | Detect, timestamp, and report the restoration of power, defined as the presence of line-side voltage within some percentage of nominal voltage for more than a programmable number of continuous seconds (nominally 60 seconds).
115 | Event/Alarm Management | Electric | Critical | Detect, date, and time stamp voltage deviation events such as high/low voltages, sags and swells of durations and magnitudes that are defined by programmable thresholds.
116 | Event/Alarm Management | Electric | Critical | Be able to configure an alarm to send based on a defined number of sag/swell cycles.
117 | Event/Alarm Management | Electric | Critical | Monitor voltage, current, per phase and phase angles to detect incorrect polarity per phase or incorrect phase sequencing on poly-phase meters.
118 | Event/Alarm Management | Electric | Critical | Monitor voltage of individual meters and allow comparisons of voltage between meters, including meters specifically placed at the start of feeders or at transformers.
119 | Event/Alarm Management | Water | Critical | Detect, timestamp, and report continuous flow leaks based on some nominal value threshold.
120 | Event/Alarm Management | Water | Critical | Detect, timestamp, and report low-flow leaks where some intervals may be zero.
121 | Event/Alarm Management | Water | Critical | Detect, timestamp, and report high flow leaks or burst events based on some nominal value threshold.
122 | Event/Alarm Management | Water | Critical | Detect, timestamp, and report backflow events.
123 | Event/Alarm Management | All | Optional | Be able to display events and alarms on a map-view.
124 | IoT Interfaces and Gateways - General | All | Optional | Read at least one 4-20 mA, 2-wire analog input from a sensor device.
125 | IoT Interfaces and Gateways - General | All | Optional | Read at digital sensor input.
126 | IoT Interfaces and Gateways - General | All | Optional | Be battery powered.
127 | IoT Interfaces and Gateways - General | All | Optional | Be capable of transmitting all collected sensor data over the AMI network at configurable intervals of, a minumum, hourly.
128 | IoT Interfaces and Gateways - General | All | Optional | Store hourly sampled data including date and time stamps for a minimum of 45 days in module memory.
129 | IoT Interfaces and Gateways - General | All | Optional | Be designed and constructed, excluding its replaceable battery, to have a life expectancy of at least 5 years.
130 | IoT Interfaces and Gateways - General | All | Optional | Be designed to have a failure rate of less than 0.5 % per year.
131 | IoT Interfaces and Gateways - Functionality | All | Optional | Be capable of receiving configuration changes and on-demand data requests over the AMI network for third-party devices.
132 | IoT Interfaces and Gateways - Functionality | All | Optional | Be capable of sending all stored data over the AMI network when queried by an on-demand data request.
133 | IoT Interfaces and Gateways - Functionality | All | Optional | Support configurable data sampling intervals at a minimum of at least 15 minute intervals.
134 | IoT Interfaces and Gateways - Functionality | All | Optional | Have the ability to time stamp and align sampling intervals in accordance with: a) for hourly intervals, on the hour; b) for 15 minute intervals, on the 15, 30, 45 and 60 minute clock positions.
135 | IoT Interfaces and Gateways - Functionality | All | Optional | Have the ability to have alternate method of capturing sampling reads when unable to do so using the fixed network.
136 | Network Configuration | All | Critical | Display and Log configuration parameters. | O
137 | Network Configuration | All | Critical | Display and Log communications network check results on all installed interfaces. | O
138 | Network Diagnostics | All | Critical | Detect, log, and report program or memory failure. | O
139 | Network Diagnostics | All | Critical | Detect, log, and report power supply or battery failure/degredation. | O
140 | Network Diagnostics | All | Critical | Detect, log and report communications link failure. | O
141 | Network Diagnostics | All | Critical | Detect, log and report excessive device temperature. | O
142 | Network Diagnostics | All | Critical | Detect, log and report microprocessor failure. | O
143 | Network Diagnostics | All | Critical | Log the communication performance and report it regularly. | O
144 | Network Diagnostics | All | Critical | Make diagnostic log information available either on-demand or by regular reporting. | O
145 | Network Diagnostics | All | Critical | Support a remotely or locally initiated test for communications connection status. Local diagnostic will include the capability to perform “ping” and obtain network interface and link information, network association status, and signal level status. | O
146 | Network Diagnostics | All | Optional | Provide managed services to the from a vendor-operated remote Network Operations Center, for a hosted solution. Managed services will include, at a minimum, alerting of network health issues and remote troubleshooting services for network components maintenance/repair. | O
147 | Network Diagnostics | All | Critical | Remotely detect network communications problems, including loss of redundant communications pathways, diminishing signal strength, or poor performance. | O
148 | Network Diagnostics | All | Critical | Provide mechanisms for remotely correcting system/component problems, which, at a minimum, shall include the ability to remotely recycle (or restart) a component. | O
149 | Network Diagnostics | All | Critical | Log the results of all remote testing and diagnostics activities and any automatic actions taken based on those results. | O
150 | Network Diagnostics | All | Critical | Provide on-demand reports that contain key diagnostics and statistics from endpoints, devices, and field communication network elements, including event/transaction status reports, trouble reports, and additions/removals. | O
151 | Network Diagnostics | All | Critical | Export meter data upon request and provide capabilities to export log data.
152 | Network Diagnostics | All | Critical | Send non-usage messages and alarms to the AMI headend that contain date/time stamp from internal meter clock, message code/type, and meter identifier.
153 | Network Diagnostics | All | Critical | Support configurable alert levels and notifications based on the severity of a problem detected and the number of endpoints affected.
154 | Network Equipment | All | Critical | Provide a battery back-up for network components (collectors, repeaters, etc.) with a runtime of at least 8 hours. | O
155 | Network Equipment | All | Critical | Provide the ability to run on solar power for network components. | O
156 | Network Equipment | All | Critical | Utilize secure communications with all authorized systems and devices, including access ports, wireless communications (such as Bluetooth), field servicing tools, and communications to any network infrastructure devices. | O
157 | Network Equipment | All | Critical | Support the following backhaul communications on network infrastructure components: Ethernet, fiber; and cellular. | O
158 | Network Equipment | All | Critical | Provide network equipment that operates in temperatures between -40 and +85 degrees Celcius. | O
159 | Network Equipment | All | Critical | Provide network equipment that complies to operating vibrations specified in IEC 68-2-6. | O
160 | Network Equipment | All | Critical | Provide network equipment that complies to operating shocks specified in IEC 68-2-27. | O
161 | Network Equipment | All | Critical | Provide network equipment that complies to humidity conditions specified in ANSI 12.20 and 5.4.3.18. | O
162 | Network Equipment | All | Critical | Provide network equipment that complies to surge conditions specified in ANSI C37.90.1 and ANSI C62.41. | O
163 | Network Equipment | All | Critical | Provide network equipment that complies to electrostatic discharge conditions specified in 61000-4-2. | O
164 | Network Equipment | All | Critical | Provide network equipment that shall utilize non-volatile memory for storing, collecting, transmistting, and retaining data. | O
165 | Network Equipment | All | Critical | Provide network equipment that shall be capable of connecting to a main voltage ranging from 120V to 480V with a tolerance of +/- 10%. | O
166 | Network Performance and Reliability | All | Critical | Meet all applicable Federal, State, and local regulatory requirements (including, but not limited to, Federal Communications Commission (FCC Title 47 C.F.R,Part 15 - Radio Frequency Devices), and applicable standards by the American National Standards Institute (ANSI)).
167 | Network Performance and Reliability | All | Critical | Support full two-way communications across the communications network (LAN, WAN, and Backhaul).
168 | Network Performance and Reliability | All | Critical | Support full two-way communications from metering endpoint devices to headend system.
169 | Network Performance and Reliability | All | Critical | Uniquely identify all endpoints and communication devices on the system.
170 | Network Performance and Reliability | All | Critical | Automatically select from redundant communications paths if available. | O
171 | Network Performance and Reliability | All | Critical | Perform data flow control after a communication or power outage to prevent resources from being overloaded. | O
172 | Network Performance and Reliability | All | Critical | Provides coverage of 100% of the current meter population represented and covers infill areas that are within the bounds of the current meter footprint. | O
173 | IoT Applications | Water | Optional | Be capable of transmitting data from and receiving at the headend water monitoring devices/sensors, such as for pressure, temperature, lead detection devices and water quality.
174 | IoT Applications | Water | Optional | Provide a platform that is capable of communicating bi-directionally from remote disconnect devices, including valves and/or meters.
175 | IoT Applications | Electric | Optional | Provide a platform for streetlight monitoring and control.
176 | IoT Applications | Electric | Optional | Provide a platform for demand response, load management, and distribution automation endpoint devices.
177 | Streetlighting | Electric | Optional | Be able to transmit events and alarms on streetlight devices, including malfunctioning devices and voltage threshold.
178 | Streetlighting | Electric | Optional | Be able to define on and off schedules for connected streetlight devices.
179 | Streetlighting | Electric | Optional | Provide the capability to perform a remote on/off command for connected streetlight devices individually.
180 | Streetlighting | Electric | Optional | Provide the capability to perform a remote on/off command for connected streetlight devices in batch mode.
181 | Distribution Automation | Electric | Optional | Support communication, configuration, and control of fault indicators, line monitors, voltage/current sensors, cap bank controllers, line reclosers, swtiches, and voltage regulators.
182 | Distribution Automation | Electric | Optional | Support prioritization of distribution automation traffic over standard metering.
183 |  |  |  | Security framework compliance requirements would need to follow the requirements specified in the draft requirements. ISO 27001 for cloud, SOC 1 for financial and SOC 2 for general controls.
184 | Security | All | Critical | Be compliant to NISTIR 7628 Rev. 1.
185 | Security | All | Critical | Be audited and certified under ISO 27001.
186 | Security | All | Critical | Be audited and certified under SOC 2 Type 1.
187 | Security | All | Critical | Be audited and certified under SOC 2 Type 2.
188 | Security | All | Critical | Receive and process data requests from other systems (e.g.. MDMS, CIS, OMS).
189 | Security | All | Critical | Not store personally-identifiable customer information.
190 | Security | All | Critical | Log invalid login attempts; retain 12 months of authentication logs success and failure.
191 | Security | All | Critical | Support a lockout for a configurable number (minimum 3) of failed login/access attempts. This applies to the AMI headend application, meter and endpoint configuration products, all field tool applications, meters and endpoints.
192 | Security | All | Critical | Support Advanced Encryption Standard (AES) for 256-bit (or higher) encryption end-to-end.
193 | Security | All | Critical | Support rolling encryption keys on a configurable basis.
194 | Security | Electric | Critical | Support ANSI C12.19/C12.18/C12.22 cryptographic solutions including clear text, plain text and cipher text communication.
195 | Security | All | Critical | Support functions which allow for secure device authentication, registration, and revocation of registration.
196 | Security | All | Critical | Supply mechanisms which audit and store all security related events including all messages, access, and modification events within the system for 90 days.
197 | Security | All | Critical | Supply a security audit store which includes the date and time of the event, type of event, subject identity, and the outcome (success or failure) of the event.
198 | Security | All | Critical | Supply access control mechanisms (i.e., Identification & Authentication mechanisms) which prevent unauthorized access of information and resource.
199 | Security | All | Critical | Log unauthorized access attempts.
200 | Security | All | Critical | Support 2-factor authentication for system access.
201 | Security | All | Critical | Restrict access to reconfiguration commands based upon user role.
202 | Security | All | Critical | Reject messages/requests that are received from unauthorized systems or devices.
203 | Security | All | Critical | Provide a configurable 'choke' to restrict the maximum number of disconnect operations allowed concurrently or on a daily basis including those disconnect requests transmitted via other systems.
204 | Security | All | Critical | Provide automated methods of preventing cross-site scripting (XSS) attacks or SQL injection attacks from compromising the databases or software functions.
205 | Security | All | Critical | Provide Network Layer IP filtering solution to allow access only from the utility's IP address to the remote server environment (especially hosted for the utility).
206 | Security | All | Critical | Securely transfer/process data between the utility and the Vendor's environment through SITE-TO-SITE VPN communication, enhanced with Multi-Factor Authentication (MFA).
207 | Security | All | Critical | Securely encrypt utility's data during the operational process, hosted at rest, and the backup stage, at the Vendor's environment (including Vendor’s contracting organization’s environment)
208 | Security | All | Critical | Offer robust disaster recovery and business continuity solutions with maximum 8 (eight) hours RTO (Recovery Time Objective) (i.e., in the event of a disaster, the services offered by the Vendor shall not exceed 8 hours downtime).
209 | Security | All | Critical | For systems hosted using third-party cloud services, such as AWS, offer a secured, logically separated IT environment in cloud consistent with the AWS_Security_Compute_Services_Whitepaper document (https://d1.awsstatic.com/whitepapers/Security/Security_Compute_Services_Whitepaper.pdf).
210 | Security | All | Critical | Offer authentication and authorization from the “utility's environment to the Vendor’s environment” and "Vendor’s environment to the cloud-hosted environment” enhanced with SSO and MFA.
211 | Security | All | Critical | Offer IP filtering for all the applications and database access to the Vendor’s environment and to the cloud environment.
212 | Service Level | All | Critical | Be capable of 97% on-demand read success executed within 60 seconds, when issued to a single meter.
213 | Service Level | All | Critical | Be capable of securing a 99% success rate or greater of daily register reads transmitted within 72 hours of read timestamp, processed at the AMI headend and available for other systems for each commodity.
214 | Service Level | All | Critical | Be capable of securing a 98% success rate or greater of daily register reads transmitted within 24 hours of read timestamp, processed at the AMI headend and available for other systems for each commodity.
215 | Service Level | All | Critical | Be capable of securing a 95% success rate or greater of all interval reads transmitted within 24 hours of read timestamp, processed at the AMI headend and available for other systems for each commodity.
216 | Service Level | All | Critical | Maintain less than 0.75% failure rate per annum for all network communications equipment over the required operating life of the system.
217 | Service Level | All | Critical | Maintain less than 1.50% failure rate per annum for all network communications equipment over the extended operating life of the system.
218 | Service Level | All | Critical | Offer 99.9% uptime for a SaaS or NaaS solution.
219 | Service Level | All | Critical | Provide, at no cost to the utility, additional network infrastructure to meet network performance SLAs if required beyond originally designed and confirmed by the propagation study.
220 | Software/Firmware Releases | All | Critical | Provide release notes prior to updates.
221 | Software/Firmware Releases | All | Optional | Allow for software releases to be able to be scheduled at Utility's discretion.
222 | Software/Firmware Releases | All | Critical | Have a rollback plan in place and be communicated to the Utility prior to any upgrades to the Software.
223 | Software/Firmware Releases | All | Critical | Retain all AMI Meter configuration and program settings, statuses, customer information, and event logs over a full Software/firmware upgrade.
224 | Software/Firmware Releases | All | Critical | Accept and install firmware upgrades remotely (over-the-air) via the AMI system in a secure manner.
225 | Software/Firmware Releases | All | Critical | Provide a secure capability to perform meter program and firmware updates in the field without removing devices.
226 | Software/Firmware Releases | All | Critical | Continue normal operation while downloading Software/firmware upgrades until instructed to switch to the new version.
227 | Software/Firmware Releases | All | Critical | Log firmware download and upgrade attempts, failures, successes, reversions, etc. with timestamp.
228 | Software/Firmware Releases | All | Critical | Report firmware upgrade status (successful or unsuccessful) to the AMI headend.
229 | System Performance and Reliability | All | Critical | Secure register reads and interval data from unknown meters for which the system has not yet received notice of the AMI meter installation, and automatically store and process these reads once the meter data synchronization completes.
230 | System Performance and Reliability | All | Critical | Be capable of receiving and processing incoming meter data on a continuous basis.
231 | System Performance and Reliability | All | Critical | Transmit and log the following information for each event: Event Timestamp, Event Type, AMI RF endpoint, and/or meter ID.
232 | System Performance and Reliability | All | Critical | Automatically retry commands when a message is not acknowledged.
233 | System Performance and Reliability | All | Critical | Record metrology data while communicating and during communication failures.
234 | System Performance and Reliability | All | Critical | Support remote configuration of all user-controllable endpoint parameters.
235 | System Performance and Reliability | All | Critical | Support remote configuration of multiple endpoints in a batched mode, via user-defined batching.
236 | System Performance and Reliability | All | Critical | Log all configuration commands and results for a minimum of 90 days.
237 | Systems Integration | All | Critical | Support Multi-Speak communication and protocols for integration to other enterprise IT systems.
238 | Systems Integration | All | Critical | Support Common Information Model (CIM) structures, commercial enterprise application infrastructure interfaces, and service oriented integration patterns for IT systems integration the utility's CIS and other enterprise IT systems.
239 | Systems Integration | All | Critical | Be capable of securing and delivering register data, interval data, and logs from endpoints and communications network components at a configurable frequency, but at least 4 times per day.
240 | Systems Integration | All | Critical | Support scheduled batch loading of meter events to other enterprise IT systems at a configurable frequency, but at least 4 times per day.
241 | Systems Integration | All | Critical | Be able to initiate an on-demand read request through a real-time interface from another authorized system (i.e., MDMS, CIS, OMS).
242 | Systems Integration | All | Critical | Be capable of delivering the results of all received alarms, outages and remote testing and diagnostic results to other systems in near-real time (within 30 seconds of receipt to the AMI headend).
243 | Systems Integration | All | Critical | Support integration with the following systems: Proposed MDMS System, Dispatch OMS
244 | Systems Integration | All | Critical | Support SSO with the following domains: Active Directory
245 | Administration | All | Critical | Be capable of identifying duplicate meter numbers.

## MDMS
ID | Category | Commodity | Priority | Requirement | Proposer Response | Proposer Comment
1 | General MDMS | All | Critical | Accept and store customer account and meter data characteristics (e.g. Meter ID, Parcel ID, account number, account address, etc.) according to the CIS data structure.
2 | General MDMS | All | Critical | Have a non-proprietary database file structure that is ODBC-compliant and SQL-compliant, and provided by a standard commercial database supplier
3 | General MDMS | All | Critical | Support configurable units of measure and interval lengths.
4 | General MDMS | All | Critical | Retain a minimum of three (3) years of interval and register reads for immediate (online) utility access.
5 | General MDMS | All | Critical | Receive and retain a minimum of three (3) years of events and alarms for immediate (online) utility access.
6 | General MDMS | All | Critical | Retain a minimum of seven (7) years of interval and register reads archived (cold storage), not inclusive of immediate (online) data.
7 | General MDMS | All | Critical | Receive and retain a minimum of seven (7) years of events and alarms archived (cold storage), not inclusive of immediate (online) data.
8 | General MDMS | All | Critical | Process meter-related issues, including, at a minimum: meters with missing reads; and unknown meters.
9 | General MDMS | All | Critical | Process consumption-related issues, including, at a minimum: meter rollover; consumption on a vacant account; zero consumption on an active account; and high and low usage.
10 | General MDMS | All | Critical | Allow for the configuration of high and low usage exception thresholds.
11 | General MDMS | All | Critical | Allow for high and low usage exception thresholds to be set based on customer parameter (e.g., customer class).
12 | General MDMS | All | Critical | Allow for tolerances in the high and low usage exception thresholds based on weather.
13 | General MDMS | All | Critical | Allow for configurable event notifications based on business rules (e.g. meter has not generated reads within X number of days).
14 | General MDMS | All | Critical | Accept the CIS rate structure for converting reads into billing determinants.
15 | General MDMS | All | Critical | Accept register reads via manual entry.
16 | General MDMS | All | Critical | Allow for configuration by an authorized user, without the need for new code development by the user, for the following validation parameters: type of service; meter type; customer; customer group; billing cycle; and rate category.
17 | General MDMS | All | Critical | Process Daylight Savings time change.
18 | General MDMS | All | Critical | Track meter events by billing account (i.e. flags, relocation, reconfiguration, tampering, etc.).
19 | General MDMS | All | Critical | Align bill for usage starting with the same date each month for coincident billing (i.e. align with billing period and billing calendar set at the utility).
20 | General MDMS | All | Critical | Upon request by CIS for specified accounts and start/end dates, provide the configured billing determinants for each account.
21 | General MDMS | All | Critical | Provide a tool to analyze and classify customers by actual usage patterns, rather than nominal customer class.
22 | General MDMS | All | Critical | Store raw reads, validated (via VEE) reads, and calculated billing determinants.
23 | General MDMS | All | Critical | Allow export of raw reads, VEE reads, and calculated billing determinants via a standard file format (e.g., .csv, .xls, etc.)
24 | General MDMS | All | Critical | Validate newly provisioned AMI meters are properly configured and communicating correctly.
25 | General MDMS | All | Critical | Report AMI meters that are not properly configured or communicating incorrectly.
26 | General MDMS | All | Critical | Be capble of identify duplicate meter numbers.
27 | General MDMS | All | Optional | Provide seperate production and test environment for the MDMS software prior to go-live.
28 | General MDMS | All | Optional | Provide seperate production and test environment for the MDMS software for the duration of the contract.
29 | General MDMS | All | Optional | Support the delivery of past-dated billing determinants to support rebilling.
30 | General MDMS | Electric | Critical | Support a minimum of 9 digits for meter reading display.
31 | General MDMS | Electric | Critical | Support the units of measure: KWH KW Voltage Power Factor
32 | General MDMS | Electric | Critical | If demand is reset at the electric meter daily, for each billing request for rates with a demand determinant, select the highest daily demand value for the billing period, for the specified meter, and deliver the demand value and corresponding date.
33 | General MDMS | Electric | Critical | Support the calculation and deliver TOU billing determinants from interval data.
34 | General MDMS | Electric | Critical | Provide a user interface to modify TOU bins (time periods, weekend, holidays, seasons).
35 | General MDMS | Electric | Optional | Support Critical Peak Pricing, including if there are one or multiple events in a single billing month.
36 | General MDMS | Electric | Optional | Support Peak Time Rebate, including calculation of baseline usage and net consumption above and below this threshold during an event.
37 | General MDMS | Electric | Optional | Support net metering by performing calculations to combine separate service and production meter readings for a solar account. (or edit to combine delivered and received channels from one meter).
38 | General MDMS | Water | Critical | Support a minimum of 9 digits for meter reading display.
39 | General MDMS | Water | Critical | Support the units of measure: Gallons and Cubic Feet
40 | On-Demand Read | All | Critical | Support on-demand meter reads by authorized users.
41 | On-Demand Read | All | Critical | Support on-demand meter reads of multiple meters at once by authorized users.
42 | On-Demand Read | All | Critical | Provide the capability to schedule an on-demand read operation to be initiated at a specified time.
43 | Operations | Electric | Critical | Convert the register reading unit of measure to a different billing unit of measure.
44 | Operations | Electric | Critical | Have the ability to truncate received meter register readings to accommodate billing determinate resolutions.
45 | Operations | Electric | Critical | Have the ability to associate multiple accounts or meters to a single customer.
46 | Performance | Electric | Critical | Have system parameters optimized for handling real-time event and alarm data (e.g. bursts, system failures, etc.) over routine and batch processes.
47 | Performance | Electric | Critical | Be capable of creating a service request to CIS or a work management system based on meter events and alarms received.
48 | Performance | Electric | Critical | Receive on-demand reads from the AMI headend within 30 seconds.
49 | Reporting | Electric | Critical | Allow for utility users to search for records based on the following characteristics: account number, name, address, premises ID number, meter body ID number, register ID number, and endpoints ID number.
50 | Reporting | Electric | Critical | Provide reporting capabilities and exportability of reports and/or data screens to other file formats (such as .csv or .xlsx).
51 | Reporting | Electric | Critical | Provide the ability to schedule a report to be generated and distributed on a user-defined-basis.
52 | Reporting | Electric | Critical | Provide the ability for users to view tables and graphs of data (at interval, daily, weekly, monthly levels) for individual meters, for a selectable date range.
53 | Reporting | Electric | Critical | Provide reports that compare multiple years (>2) of historical data side-by-side.
54 | Reporting | Electric | Critical | Provide reporting tool to allow user-defined date range in graphical and tabular formats.
55 | Reporting | Electric | Critical | Render meter records on a map view based on report results.
56 | Reporting | Electric | Critical | Provide configurable system homepages with reports / KPI / other depending on the user needs (e.g., revenue health, conservation program health, outage management health, revenue protection health).
57 | Reporting | Electric | Critical | Have elements of an individual user's system homepage that can be customized using existing tools within the MDM.
58 | Reporting | Electric | Critical | Provide reports of customers with leaks due to continuous consumption alerts based on configurable threshold for customer leak detection.
59 | Reporting | Electric | Critical | Provide zero consumption reporting; identify meters with zero consumption and the account is inactive, as well as zero consumption on active accounts.
60 | Reporting | Electric | Critical | Provide vacant consumption reporting; identify inactive accounts with consumption.
61 | Reporting | Electric | Critical | Provide consumption forecasting tools that can identify consumption patterns and predict future consumption based on historical trends and weather predictions.
62 | Reporting | Electric | Critical | Provide revenue analysis tools to support, at a minimum: revenue profiling daily, monthly and annually; and revenue profiling for billing customer classes or based on user-selected virtual metering.
63 | Reporting | Electric | Critical | Provide tools for reporting power quality excursions.
64 | Reporting | Electric | Critical | Incorporate external data (weather, property, climate) into reporting and analytical reporting tools.
65 | Reporting | Electric | Critical | Provide tools and/or reports to identify EV chargers in service territory.
66 | Reporting | Water | Critical | Provide water conservation consumption reporting to support, at a minimum: the ability to identify accounts with high water consumption based on monthly consumption targets and non-watering days of the week.
67 | Security | All | Critical | Have collected metering data to be owned by the utility; and that this data may not be used by any other party unless prior authorization / approval is granted.
68 | Security | All | Critical | Provide a secure login (e.g. authentication with LDAP) in compliance with ISO27001 to prevent access by unauthorized users.
69 | Security | All | Critical | Provide two factor authentication for system access.
70 | Security | All | Critical | Support user authentication and authorization by role in compliance with ISO27001.
71 | Security | All | Critical | Provide authorized users’ access to audit logs in compliance with ISO27001 that shall track all changes to interval usage, register meter reads and configuration data.
72 | Security | All | Critical | Secure web interfaces (i.e. ‘https’) and utilize appropriate encryption and authentication.
73 | Security | All | Critical | Secure / encrypt all file transfers to other systems (e.g., via SFTP, AES 128-bit encryption, RSA key, etc.).
74 | Security | All | Critical | Support a lockout for a configurable number (minimum 3) of failed login / access attempts.
75 | Security | All | Critical | Enable and support IP filtering.
76 | Security | All | Critical | Provide automated methods of preventing cross-site scripting (XSS) attacks or SQL injection attacks from compromising the databases or software functions.
77 | Security | All | Critical | Provide Network Layer IP filtering solution to allow access only from the utility's IP address to the Vendor environment (especially hosted for the utility).
78 | Security | All | Critical | Securely transfer/process data between the utility and the Vendor's environment through SITE-TO-SITE VPN communication, enhanced with Multi-Factor Authentication (MFA).
79 | Security | All | Critical | Securely encrypt utility's data during the operational process, hosted at rest, and the backup stage, at the Vendor's environment (including Vendor’s contracting organization’s environment)
80 | Security | All | Critical | Offer robust disaster recovery and business continuity solutions with maximum 8 (eight) hours RTO (Recovery Time Objective) (i.e., in the event of a disaster, the services offered by the Vendor shall not exceed 8 hours downtime).
81 | Security | All | Critical | Offer 99.8% up-time in the Service Level Agreement (SLA).
82 | Security | All | Critical | For systems hosted using third-party cloud services, such as AWS: offer a secured, logically separated IT environment in cloud consistent with the AWS_Security_Compute_Services_Whitepaper document (https://d1.awsstatic.com/whitepapers/Security/Security_Compute_Services_Whitepaper.pdf).
83 | Security | All | Critical | Offer authentication and authorization from the “utility's environment to the Vendor’s environment” and "Vendor’s environment to the cloud-hosted environment” enhanced with SSO and MFA.
84 | Security | All | Critical | Offer IP filtering for all the applications and database access to the Vendor’s environment and to the cloud environment.
85 | System Admin | All | Critical | Store utility-accessible audit logs for up to three (3) years or a configurable length of time up to ten (10) years.
86 | System Admin | All | Critical | Align the read delivered for billing to the date calendared by CIS.
87 | Systems Integration | All | Critical | Support real-time integration methods (e.g., MultiSpeak, SOAP, XML, Restful API, etc.)
88 | Systems Integration | All | Critical | Provide updates to the MDM Integrations within 3 months of the General Availability of new versions of the AMI Headend System or MDMS.
89 | Systems Integration | All | Critical | Provide synchronization tracking method for request for file exchange with other IT systems, logging request for file exchange, and completion of file exchange requests by MDMS.
90 | Systems Integration | All | Critical | Support the transfer of data to and from the AMI headend and other utility systems using real-time communication protocols or other common interface models to ensure transfer of data.
91 | Systems Integration | All | Critical | Accept scheduled batch files.
92 | Systems Integration | All | Critical | Originate and receive real-time data transfers with the AMI headend (i.e., on demand read request/response).
93 | Systems Integration | All | Critical | Support an interface with email and SMS to send alarms or status reports to designated recipients.
94 | Systems Integration | All | Critical | Support integration with the following systems: Northstar CIS, Silverblaze Customer Portal.
95 | Systems Integration | All | Critical | Support SSO with the following domains: Active Directory
96 | VEE | All | Critical | Have the ability to automatically estimate missing or invalid register reads and interval data using configurable estimation rules.
97 | VEE | All | Critical | Have the ability to clearly identify to the user any sets of reads or data requiring manual verification or editing.
98 | VEE | All | Critical | Provide a user interface and tools for viewing, verifying and changing register reads and interval data.
99 | VEE | All | Critical | Receive, process and store register reads and interval data from AMI meters where data was previously identified as missing and estimated without delete any previously received or estimated data.
100 | VEE | All | Critical | Have the ability to identify scenarios where estimated data is provided for billing and subsequently, actual read data is received, and should store both the estimate and actual.
101 | VEE | All | Critical | Not overwrite, replace or version valid data with estimated data unless replacement occurs by a manual process.
102 | VEE | All | Critical | Have the ability to identify reads or data that requires manual verification or editing and provide a user interface for verifying and changing register reads and interval data. An audit trail of all changes should be provided.
103 | VEE | All | Critical | Have the ability to receive, process, and store reads from external sources (e.g. MV-90; manually captured reads, etc.).
104 | VEE | All | Critical | Have the ability to assign VEE rule sets to each data channel to allow different VEE behavior for different channels of data.
105 | VEE | All | Critical | Support the modification of existing VEE rules or creation of new VEE rules.
106 | VEE | All | Critical | Estimate interval data based on the characteristics of the meter.
107 | VEE | Electric | Critical | Have the ability to automatically validate register reads and interval data received from AMI meters to identify missing or invalid data using configurable validation rules.
108 | Virtual Metering | All | Critical | Provide virtualization of meters using from attributes synchronized with the CIS system (e.g. by pressure zone, meter type or size, customer class, rate group, feeder, etc.).
109 | Virtual Metering | All | Critical | Provide virtualization of meters using ad hoc meter groups (e.g. via a polygon on a map).
110 | Virtual Metering | All | Critical | Be able to dyanmically update a virtual meter by adding or removed meters from the virtual meter group based on rules for that group.
111 | Virtual Metering | All | Critical | Be able to establish utility user-defined alarm thresholds for each virtual (aggregation / DMA) meter.
112 | Virtual Metering | All | Critical | Totalize/sum usage channels for assigned meters in a virtual meter.
113 | Virtual Metering | All | Critical | Delivery billing determinants for virtual meters using standard billing integrations.
114 | Virtual Metering | All | Critical | Calculate units of measure from the sub-meters of a virtual meter, such as demand.

## Water Metering
ID | Category | Commodity | Priority | Requirement | Proposer Response | Proposer Comment
1 | Lids & Meter Boxes | Water | Critical | Be compliant to the dimensions outlined in specifications.
2 | Lids & Meter Boxes | Water | Critical | Be a reinforced polymer material.
3 | Lids & Meter Boxes | Water | Critical | Have Radio Frequency (RF)-Transparency.
4 | Lids & Meter Boxes | Water | Critical | Lids should be black or grey in color.
5 | Lids & Meter Boxes | Water | Critical | Have sufficient weight or a locking mechanism that prevents them from being dislodged or from floating.
6 | Lids & Meter Boxes | Water | Critical | Have a ferrous element (e.g. section of rebar) that enables them to be discovered by a metal detector when buried
7 | Lids & Meter Boxes | Water | Critical | Conform to chemical conditions tested in accordance with ASTM D543-06.
8 | Lids & Meter Boxes | Water | Critical | Be constructed from AASHTO-recognized materials, capable of withstanding AASHTO M306 Sect 6 loads, at a minimum, for all lids with deliberate vehicular traffic applications.
9 | Lids & Meter Boxes | Water | Critical | Conform to UV conditions tested in accordance with ASTM G154-06.
10 | Lids & Meter Boxes | Water | Critical | Have a static coefficient of friction to mitigate slipping hazard, as tested in accordance with ASTM C1028-07.
11 | Lids & Meter Boxes | Water | Critical | Withstand impacts as described in ASTM D2444-05.
12 | Lids & Meter Boxes | Water | Critical | Be non-flammable or exhibit a burning rate as specified in ASTM D635-06.
13 | Lids & Meter Boxes | Water | Critical | Resist wear by abrasion in accordance to ASTM C501.
14 | Meter - Functionality | Water | Critical | Provide electronic vendor meter inventory file with deliveries.
15 | Meter - Functionality | Water | Critical | Be capable of continuous operation in dust or a submerged environment, of at least IP 68 rating or higher, per IEC 60529.
16 | Meter - Functionality | Water | Critical | Have connections that shall be waterproof and corrosion proof.
17 | Meter - Functionality | Water | Critical | Measure consumption in gallons.
18 | Meter - General | Water | Critical | Meet AWWA C700 series standards for Minimum Test Flows, and Nominal Flow Limits For Specified Meter Size and Type
19 | Meter - General | Water | Critical | Contain no lead according to CFR 141.43 outlined by the Environmental Protection Agency.
20 | Meter - General | Water | Critical | Have accuracy tests that shall be conducted in accordance with AWWA test methods and meter standards.
21 | Meter - General | Water | Critical | Provide electronic vendor meter factory accuracy test file with deliveries.
22 | Meter - General | Water | Critical | Have a permanently affixed serial number.
23 | Meter - General | Water | Critical | Be supplied with a scannable bar code label affixed to the meter.
24 | Meter - General | Water | Critical | Be warranted free from defects in materials and workmanship for twenty four (24) months from date of shipment or eighteen (18) months from date of installations
25 | Meter - Other Applications | Water | Optional | Be available with an optional integrated pressure monitor, for new meters.
26 | Meter - Other Applications | Water | Optional | Be available with an optional integrated temperature monitor, for new meters.
27 | Meter - Register | Water | Critical | Meet the latest AWWA C700 series Encoder-Type Remote-Registration Systems for Cold-Water Meters
28 | Meter - Register | Water | Critical | Be compatible with AMI water endpoints
29 | Meter - Register | Water | Critical | Provide reads to the AMI water endpoints in units of no greater than 1 Gallon
30 | Meter - Register | Water | Critical | Be capable of being read both manually and electronically
31 | Meter - Register | Water | Critical | Have a leak detector indicator or equivalent means of indicating minimal flows of water.
32 | Meter - Register | Water | Critical | Should have a cap to prevent dirt from interfering with the visual inspection of the register
33 | Meter - Register | Water | Critical | Be waterproof and corrosion proof.

## Installation Services
ID | Category | Commodity | Priority | Requirement | Proposer Response | Proposer Comment
1 | Data Capture | All | Critical | Capture clear and legible digital images a minimum of: (1) pre-install meter site; (2) legacy meter face for out read;(3) new meter face immediately following install; (4) new endpoint serial number; (5) picture of spigot clearing, (6) site as left by installer.
2 | Data Capture | All | Critical | Capture images with an accurate date / time stamp.
3 | Data Capture | All | Critical | Capture images searchable by meter number assigned by utility or alternatively another unique identifier as determined by utility.
4 | Data Capture | All | Critical | Capture multiple images for meters with multiple registers.
5 | Data Capture | All | Critical | Review and validate 100% of meter reads that have been entered in their work order management system against the meter face photo taken during installation.
6 | Data Capture | All | Critical | Provide daily data uploads to proposed vendor WOMS site.
7 | Data Capture | All | Critical | Provide completed work orders that pass data validation to utility within 2 business days of installation.
8 | Data Capture | All | Critical | Collect GPS coordinates within 3m-5m accuracy and provide the meter location in reference to the premise.
9 | Data Capture | All | Critical | Perform a visual inspection, document, photograph, and notify Utility within 1 business day of new meter, tamper, or theft conditions found during installation.
10 | Data Capture | All | Critical | Perform a visual inspection, document, photograph, and notify Utility in near-real-time of potential damage, malfunction, or other critical issues (e.g., adverse conditions/indicators, safety hazards, infrastructure concerns, etc.) found during installation that would signal an immediate work stoppage for the meter.
11 | Data Capture | All | Critical | Verify meter/endpoint inventory is in stock and ready to be installed, and that serial numbers are not duplicated.
12 | Data Capture | All | Critical | Barcode scan transactions involving hardware to ensure data integrity of meters, registers and endpoints.
13 | Data Capture | All | Critical | Integrate and/or export meter exchange data (meter ID, last meter read, new meter read, installation date, meter model, location, GPS, service order number, etc.) to a format acceptable to CIS.
14 | Disposal | All | Critical | Dispose of removed meters, registers, ancillary hardware, and all associated materials from the Worksite.
15 | Disposal | All | Critical | Utilize environmental-safe procedures when disposing meters, hazardous material (e.g. batteries) and provide manifest of disposed materials.
16 | Installation | All | Critical | Provide a supervisor-to-installer ratio of at least 10-to-1.
17 | Installation | All | Critical | Provide secure warehouse space for staging new inventory and storing removed meters.
18 | Installation | All | Critical | Provide trailer, storage, bathrooms, electricity, and fencing to secure, as necessary.
19 | Installation | All | Critical | Provide own equipment for handling materials, such as a forklift.
20 | Installation | All | Critical | If an installed meter is discovered to have failed within one year of installation, as a result of installation negligence, be responsible for replacing the meter or providing a credit to the utility.
21 | Installation | All | Critical | Notify customer prior to meter replacement with advance postcard (double-sided, with color printing), and provide a door hanger (double-sided, with color printing) after installation complete or non-complete.
22 | Installation | All | Critical | Have a published process for resolving meter installation issues prior to making them an Return To Utility.
23 | Installation | All | Critical | Make no less than three attempts to complete/resolve any given installation before tranferring an Unable to Complete (UTC) / Return to Utility (RTU), unless due to existing service damage or tampering.
24 | Installation | All | Critical | Coordinate with the utility for gated community access.
25 | Installation | All | Critical | Coordinate with the utility for access to locked vaults.
26 | Installation | All | Critical | Clean out meter box of dirt, water and other debris to registers necessary to facilitate meter/endpoint installation, and remove dirt and debris from the site.
27 | Installation | All | Critical | Install equipment in accordance with the manufacturer’s specifications and recommendations.
28 | Installation | All | Critical | Verify that the new meter and/or endpoint is fully functional, properly installed, and that the customer is with the same status (on/off) before leaving a site.
29 | Installation | All | Critical | Provide logs of errors / damage resulting from installation by the meter installation contractor, or of any customer complaints, including caller’s name, address, account number if available, date and time of call, nature of problem, the action taken and the resolution.
30 | Installation | All | Critical | Respond within one (1) hour of receiving a complaint call and arrive at customer’s premises ready to correct any problems resulting from errors / damage by the installer, unless otherwise directed by the utility.
31 | Installation | All | Critical | Resolve errors / damage resulting from installation by the installer within 24 hours, unless situation results in RTU.
32 | Installation | All | Critical | Handle non-binding or non-communication endpoint issues. Utility will not pay for installation services until it is verified that the meter is communicating with the proper information to the head end system.
33 | Installation | All | Critical | Verify meter is installed and registering properly and not reversed.
34 | Installation | Electric | Critical | Capable of installing single and polyphase meters
35 | Installation | Electric | Optional | Be capable of replacing CT meters
36 | Installation | Water | Critical | Be able to perform ad hoc lid replacements.
37 | Installation | Water | Critical | Correct all leaks related to the installed meters (e.g., damaged meter, washers, etc.)
38 | Installation | Water | Critical | Be responsible for correcting at-fault breaks in the service line using similar material type for up to 3' before and after connection to the meter.
39 | Installation | Water | Critical | Flush customer line after meter installation to be free of air and debris, if possible and remediate contaminated water supplied to the customer as a result of meter installation, including, but not limited to, disinfection, flushing, and sampling.
40 | Other | All | Critical | Provide a call center for customer to coordinate appointments, address customer complaints, and answer question on the project and installation procedures, supporting English and Spanish language options.
41 | Other | All | Critical | Remove employees from the project upon request from the utility as deemed necessary by the utility.
42 | Other | All | Critical | Have the designated project manager along with key team members onsite and participating in weekly project status meetings, providing written reports on: actual versus projected deployment numbers; unable-to-complete and return-to-utility metrics; issue log (if needed), including RTU and UTC reports; quality assurance results; and inventory audit results.
43 | Safety & Appearance | All | Critical | Have vehicles consistent in appearance and approved by the utility.
44 | Safety & Appearance | All | Critical | Have all field personnel wear hi-vis, easily recognizable and consistant uniforms or safety vest containing company name, as well as prominently displayed utility-approved photo identification badges.
45 | Safety & Appearance | All | Critical | Be trained on basic customer service, how to address customer inquiries and when to transfer a customer to the utility.
46 | Safety & Appearance | All | Critical | Leave the customer site in as good or better condition before and after servicing.
47 | Safety & Appearance | All | Critical | Provide proof of background checks, which cover at minimum: criminal history, sex offender registry check, and driver’s license verification.
48 | Safety & Appearance | All | Critical | Provide pre-employment 8-panel drug and alcohol screening, random testing during employment, and a policy on identification of intoxication and testing based on reasonable suspicion.
49 | Safety & Appearance | All | Critical | Provide safety training for employees.
50 | Safety & Appearance | Electric | Critical | Have installer wear approriate PPE, including flame-retardant clothing, face shields, and gloves.
51 | Safety & Appearance | Water | Critical | Be capable of servicing large meter vault in a confined space with proper access certification.
52 | Scheduling | All | Critical | Complete phone calls for non-complete site visits.
53 | Scheduling | All | Critical | Attempt to notify customer prior to shutting water off, and have a process for handling a moving meter.
54 | Scheduling | All | Critical | Assist/coordinate meter installation scheduling according to the outlined deployment strategy, with the utility retaining the right to prioritize routes, neighborhoods, and customers, as needed.
55 | Scheduling | All | Critical | Be available during utility's regular business hours (6:45 a.m. - 3:30 p.m.), with work beyond normal business hours coordinated with the utility at least two weeks in advance.
56 | Scheduling | All | Critical | Complete only routes pre-authorized for work by utility Project Manager.
57 | Survey | Water | Optional | When observable, note any galvanized service lines leading to or from a meter.
58 | Work Order Management System | All | Critical | Support storage for data capture requirements identified above and up to 10 photos per installation. Utility access to the storage will be provided for a minimum of 1 year after project completion. Provide training on web interface to contractor provided Work Order Mangement System.
59 | Work Order Management System | All | Critical | Provide all work order information to utility at the end of deployment in CSV, Excel, or other standard file format, in addition to labelled photos.
60 | Work Order Management System | All | Critical | Provide a work order management system that can be web accessed by at least six (6) utility staff concurrently.
61 | Work Order Management System | All | Critical | In the work order management system, provide summary view of planned, incomplete and completed work orders that is updated daily.
62 | Work Order Management System | All | Critical | Provide lookup capabilities for individual work order details, with ability to look up by meter no., account no., or other identifiable information.
63 | Work Order Management System | All | Critical | Provide reports or filtering tools to view route completion.
64 | Work Order Management System | All | Critical | Have a WOMS capable of accepting periodic updates to the database as customers are added/changed within the existing utility meter reading routes.

## Sheet2 (hidden)
Integration | Support export/import ability to Asset Framework and Milsoft | Move to Integration discussion
Integration | Support meter to distribution phase identification | Move to Integration discussion. Identify hardware requirements for the phase identification
Note on A6: Author: Not sure if this is the appropriate place to put Integration Categories?

## Sheet1 (hidden)
Current Base
Future Base Release
Modification
Third Party System
Customization
Not Provided